|  | CFAS Enterprises Inc. After Market Utility Power Equipment Brokerage Mailto:Staff@CFASPower.com Turbine URL: http://CFASPower.com/Inventory.html Reciprocating URL: http://CFASPower.com/Recips.html |
| --- | --- |

GTG_1316JL_GELM5000.doc

1 X Usd GE LM5000STIG 47MW/11Kv/50hz/ Gas Turbine Plant

Price:			USD $3MM Removed and Packed

The Scope Of Supply Includes GTG, HRSG, Main Transformer And All Auxiliary Equipment.

The Serial Number For The GT:			GE7LM5000-GE-NDBG-G03 Is SN474-142

Generator Model: 					Brush BDAX7-290ER

HRSG:							Deltak DINO4530 HRSG

Main Transformer Model: 				SF8-63000

Rating:							110,63000 kva

Connection:						YN.D11

Voltage:						121x2.5%/11.5kv

Current:						300.6/3163A

Frequency:						50Hz

Cooling:						Natural Cooling/Fan

The Steam Generated By The HRSG Is Injected Into The Gas Turbine (STIG) , Therefore, There Is No Steam Turbine.

The Control System Has Converted From Woodward DCS 501 Into Siemens PCS7

Major Overhaul Is Done By MTU.

Used Gas Turbine LM5000STIG

Manufacturer:						GE Stewart & Stevenson

Model: 						LM5000STIG

Year Of Manufacture:					1990

Total Running Hour:					28780

Fuel:							Light Diesel

Ambient Temp:					15 C

Atmospheric Pressure:				101.325kpa

R.H. L							60%

Generator Output Voltage:				11.5kv

Power:							Factor:0.9

Frequency:						50Hz

Speed:							3000 rpm

Inlet Pressure Loss:					4 In H2O

Outlet Pressure Loss: 				Single Cycle 8 In H2O STIG 10 In H2O

Single Cycle Output Power:				31427kw

Heat Rate:						1O3O5BTU/kWH

STIG Power Output:					47020kw

Heat Rate:						8660 BTU/kWH

Noise Level:						90dB (A) At 1m From Cabin,1.5m Height 								From Platform

- Gas TurbineManufacturer: 			G.E. USA

Combustion System: 					GE7LMS000-GE-NDBG-G05 474-142

Low Pressure Compressor:				5 Stages

Ratio:							2.5

High Pressure Compressor: 				14 Stages

Ratio:							12

Combustion Chamber:				Ring Type 30 Fuel Nozzles

High Pressure Turbine:				2 Stages

Low Pressure Turbine:				1 Stage

Low Pressure Rotor Speed: 				Max. 4325 rpm

High Pressure Rotor Speed:				Max.10800 rpm

- Power Turbine

- Model: 					GET-5000-GO3

- No Of Stage:					3

- Speed:						3000 rpm

3. Lub Oil Supply Pressure: 			20-85 psig

4. Lub Oil Return Pressure:				15-75 psig

5. Start Up System:					Hydraulic Speed Converters

6. AC Generator:					Brush Electric Machines Ltd

Model:							1 Class. D,Partll

Rate Power						52244kva

Power Factor:						0.9

Output Voltage:					11.5kv

Frequency:						50hz

Phase:							3

Connection:						Star

Speed:							3000 rpm

Cooling:						Air Cooled

7. GT External Lub Oil System

Oil Tank Cap:						200 Gal (832.7 lit)

Lube Oil Filter Spec:					6 micron

Lube Oil Return Spec:				6 micron

Cooling System:					Dual Air/Oil Cooler

Lib Oil Spec:						MIL-L-23699 Or MIL-L-7808

8. Generator Lube Oil System

Oil Tank Cap:						500 gal (1 892.5 lit)

Filter Spec:						6

MicronCooling System: 				Dual Gas/Oil Cooler

Oil Supply: 						Generator Drive Oil Pump, AC Oil 								Pump And High Level Oil Tank

9. Fuel System

Filter Spec:						19 micron

Supply Pressure:					10-15OºPSIG

Oil Temp Max: 					150º F(65.5º C0

Supply Cap: 						65 gal/min(246 lit/min)

Fuel Oil Spec: 					Light Diesel To GE Standard

10. Steam Return System

High Pressure Steam Flow: 				Approx. 72000 lb/hr

Low Pressure Steam Flow: 				Approx. 72000 lb./hr

11. Off Line Washing System

Water Pressure: 					15-65 psig

Water Tank Cap:					25 gal (94.63 lit)

Meter Air Pressure:					85-120 psig)

12. Hydraulic Start Up System

Oil Tank Cap:						40 gal (151.4 Lit)

Oil Filter Spec:					10 Micron

Oil Pump Cap:						20 gal/min (340 PSIG)

Circular Pump Cap:					Max. 56 gal/min(5200 psig)

Start Up Motor Cap: 					Variable Cap.0-6.53

CIDHydraulic Oil Spec: 				MIL-H- 1767212075TH

13. Ventilation System

Total Air Flow:						373000 cu. ft./min (10444 cbm/min)

GT Inlet:						275000 cu. ft./min (7700 cbm/min)

Air Flow To GT Cabin: 				1 Fan 60000 cu. ft./min (1680 cbm/min)

2 Fans 12000 cu./ft../min (3360 cbm/min)

Air Flow To Generator Cabin:				1 Fan 38000cu.ft./min(1064 cbm/min)

2 Fans 76000 cu. ft./min(2128 cbm/min)

14. Total Dimension

Total Length 80ft.  In( 24.32m)

Width

Main Cabin:						13ft. 6in (4.104m)

Including Air Filter And Rain Sheath:			46ft. 9In (14.212m)

Total HeightMain Cabin:				14ft. 6In (4.408m)

Include Air Filter Housing:				36ft. (11m)