|  | CFAS Enterprises Inc. After Market Utility Power Equipment Brokerage Mailto:Staff@CFASPower.com Turbine URL: http://CFASPower.com/Index.html Reciprocating URL: http://CFASPower.com/Recips.html |
| --- | --- |
| GTG_1332PE_Althom6541.doc |  |

2 x Alstom PG6541B 35MW Each 50Hz Combined Cycle Power Plant

Description: 2 x Alsthom PG6541-B Gas Turbine Gensets - Manufactured in 1991/installed 1993. 35MW each @ 50Hz. Operating hours 28524/31267. Last pre OH maintenance was conducted in 2000. Includes HRSG built by Stein. Located in China.

Asking Price:			USD $9.765MM Both

Steam Turbine And Main Transformer NOT Include

Manufactured by					France EGT—ALSTHOM

Model							PG6541-B

Manufactured Date					End Of 1991

Operation Date					March 1993

Total Running Hours					1#GT 28524hours

2#GT 31267hours

Last OH:						Both Units were OH by GE Singapore in July,2004

TSO:							2000 hrs

Operation Mode					Single Or Combined Cycle

Rotation Direction					Look From Control Cabin To Generator-								Clockwise

Fuel Type						Light Diesel Or Heavy Fuel Oil

Start Up Method					Diesel Engine Start Up

Basic Protection					Micro Computer Protection

Cooling Water Mode					Internal Circulation

Rated Output Power					35MW

Inlet Temp						Ambient Temp

Exhaust Temp						527 544

Turbine Inlet Temp					1074 1104

Inlet Air Pressure Drop				125mmh2o 1.2258kpa

Exhaust Pressure Drop

Simple Cycle						75 Mmh2o

Combined Cycle 					300 Mmh2o

Heat Rate

Simple Cycle 						11935 11716KJ/KWH

Combined Cycle 					8044	7914KJ/KWH

Heat Consumption					Simple Cycle 402.2×106KJ/H 417.7×106KJ/H

Efficiency						Simple Cycle 30.16% 30.73

Combined Cycle 					44.75% 45.49%

Air Flow						138.3kg/S(100%Speed ISO)

Compressor Stages					17stages

IGV Mode						Hydraulic Adjustable

Inlet Pressure						1013mbar

Compressor Mode					Axial Flow

Compressor Ratio					11.8

Compressor Speed					5114rpm

Turbine Mode						Single Axial Axial Flow

Turbine Stages					3 stages

Turbine Speed					5114rpm

Generator Manufacturer				Alsthom

Generator Model					T190-240

Generator Output Voltage				11kv

Generator Frequency					50hz

Excitor Model ,Power					Tkj70-10 126.5kw

Generator Output Power				37.1mw

Start Up Engine Model Power			12v71t、630hp

Start Up Drive Clutch

Torque Converter					Hydraulic Torque Converter

Electro-Hydraulic Rotator

Auxiliaries Gear Box Model				AA51DA

Load Gear Box Input Speed: 				5114 rpm

Output Speed						3000 rpm

Turbine control					MARK

HRSG brand						France STEIN

HRSG type: 						Vertical Non-Duct Heating Dual Pressure Force 							Circulation

HRSG Flowrate:					10.363.6t/H

Steam Pressure:					53×105pag

Steam Temp						492

Last Maintenance date: 				July 2000