|  | CFAS Enterprises Inc. After Market Utility Power Equipment Brokerage Mailto:Staff@CFASPower.com Turbine URL: http://CFASPower.com/Inventory.html Reciprocating URL: http://CFASPower.com/Recips.html |
| --- | --- |
| GTG_1515DE_3x7FA.doc |  |

3 x Unused 2004 GE Fm PG7241FA 171Mw Each Gas 60Hz 18KV DLN Generators

Asking Price As/Is:						US $30MM Each

Location: USA

Natural Gas

Starting: Static Start

Air Filtration: Two Stage Static

Exhaust System Axial Exhaust

Emission Control Gas-Dry Low Nox

Outdoor Enclosure Turbine and Accessory Compartments

Off-Base Acoustic Enclosure Turbine and Accessory Compartments

Off-Base Acoustic Enclosure Turbine Compartment

Generator- (Location: USA)

Model 7FH2

Cooling Hydrogen

Frequency 60 Hz

Power Factor (PF) 0.85 Lagging

Terminal /Voltage 18.0 KV

Generator Excitation EX2000P-Static Bus Fed

Outdoor Enclosure Load Compartment

On-Base Lagging Accessory Base

Control Systems

Turbine-Generator SPEEDTRONIC mark VI

- All auxiliary equipment for Unit 1 is stored in USA

5.1 Gas Turbine Systems

5.1.1 Gas Turbine

- Base-mounted PG7241 (FA) 60 Hz gas turbine including:

- Modulating IGV

5.1.2 Combustion System

- Dry Low NOx combustion system

- Combustion system features

- Thermal barrier coated liners

- Nimonic transition pieces

- Reuter Stokes SiC flame detectors

- With compressor inlet heating

5.1.3 Fuel Systems

5.1.3.1 Gas Fuel System

- Natural gas only

- Stainless steel gas piping

- Orifice type gas flow measurement system

- Single gas strainer

- Gas fuel temperature supplied per GEI-41040F- Heater by Owner

- Gas fuel valves on accessory base

- Gas fuel cleaning equipment

- Fuel gas scrubber, Duplex

5.1.4 Lubricating and Hydraulic Systems

5.1.4.1 Pumps

- AC motor driven dual lube oil pumps

- AC motor driven dual hydraulic pumps

- Used for jacking oil also

- DC motor driven, emergency lube oil pump

- AC/DC motor driven auxiliary generator seal oil pump

5.1.4.2 Filters and Coolers

- Dual lube oil system filters

- Dual hydraulic oil filters

- Dual lube oil coolers

- With 90-10 copper-nickel straight-tubes

- ASME code stamp

- Lube oil coolers

- Lube oil filters

5.1.4.3 Lube Oil Piping

- 304L stainless steel lube oil feed pipe

- Carbon steel lube oil drain pipe

- Lube system valve stainless steel trim

5.1.4.4 Mist Elimination

- Lube vent demister

5.1.4.5 Oil Reservoir

- With heater for -20°F

5.1.4.6 Instrumentation

- Delta pressure switches for lubrication and hydraulic oil filters

- Lubrication oil header pressure transmitter

- Lubrication oil tank level transmitter

- Lubrication oil filter differential pressure transmitter

- Hydraulic oil supply pressure transmitter

5.1.5 Inlet System

- Inlet system arrangement

- Up and forward inlet system arrangement

- Inlet compartment supports straddle ductline

- Inlet filtration

- Two-stage static filter; prefilter and high efficiency filter

- Filter media (high humidity)

- 50 micron moisture separator

- Weather protection on inlet filter compartment

- Inlet system differential pressure indicator

- Inlet system differential pressure alarm

- Inlet filter compartment support steel

- Caged ladder access to inlet filter compartment

- Left hand access to inlet filter compartment

- Inlet filter compartment interior lighting

- Inlet heating

- Bleed heat manifold located in duct

- DLN premix turndown inlet bleed heat control

- Compressor pressure ratio operating limit bleed heat control

- Inlet bleed heat control valve(s)

- Inlet ducting

- Inlet silencing

- Inlet expansion joint

- Inlet 90 degree elbow

- Inlet transition piece

- Inlet ducting support steel

- Diluent injection instrumentation

- Compressor inlet humidity sensor

- Compressor inlet temperature thermocouple

- Inlet system atmospheric protection

- Zinc rich paint inside and outside of inlet filter compartment

- Epoxy overcoat inside and outside inlet filter compartment

- Galvanized inlet filter compartment support steel

- Zinc rich paint inside and outside of inlet ducting with epoxy top coat inside ducting

- Epoxy top coat outside of inlet ducting

- Stainless steel inlet silencing perforated sheet

- Galvanized inlet ducting support steel

5.1.6 Exhaust System

5.1.6.1 Arrangement

- Exhaust diffuser with an axial exit

- Exhaust expansion joint

5.1.7 Couplings

- Rigid load coupling

- Load coupling guard

5.1.8 Gas Turbine Packaging

- Lagging and enclosures

- On-base accessory compartment lagging

- Off-base acoustic enclosure for turbine only

- ]Off-base load coupling compartment enclosure

- Acoustic barrier wall around exhaust diffuser

- Compartment ventilation, pressurization and heating

- Dual turbine compartment vent fans

- Dual accessory compartment vent fans

- Dual load compartment vent fans

- Heated turbine and accessory compartments for humidity control

- Plant arrangement

- Turbine designed for installation outdoors

- Right hand accessory module

- Exterior unit walkways by customer, mounting pads by GE

- Interior unit walkways

- Turbine and accessory base painting

- Standard primer only

- UBC Seismic Zone 4 (except for inlet and exhaust)

- UBC Seismic Zone 2A for inlet and exhaust

- Hazardous area classification

- NEC Class1, Group D, Division 2

- Turbine compartment

- Natural gas fuel compartment

- Special features

- Dual (metric-English) indicators and gauges

5.1.9 Fire Protection System

- Fire detection system

- Turbine and accessory compartments

- Smoke detection system

- Control cab/PEECC

- Compartment warning signs

- CO2 supply system

- One low pressure CO2 tank per unit

- Tank suitable for 0-120°F (-18 to 49°C)

- Fire protection piping

- Turbine and accessory enclosures

- Hazardous atmosphere detectors in turbine and gas fuel compartments

- CHx detectors - natural gas compartment

- CHx detectors - turbine gas compartment

- Hazardous atmosphere detector readout

- CHx

5.1.10 Cleaning Systems

- On base piping for on and offline compressor water wash system

- Water wash skid

- Water storage tank

- Skid enclosure

- Single skid per site (1 skid per 3 units)

5.1.11 Cooling Water System

- Cooling system temperature regulating valve

5.1.12 Starting Systems

- Static start

- Generator start with inverter/regulator

- Static start isolation transformer

- Oil filled

- Rotor turning systems

- Turning gear and motor for rotor cooldown

- Rotor indexing (borescope inspection)

5.1.13 Miscellaneous Systems

5.1.13.1 Special Systems

- Exhaust frame blowers on turbine compartment roof

5.2 Generator

5.2.1 General Information

- Hydrogen cooled generator with conventionally cooled armature

- Outdoor installation

- 60 Hz generator frequency

- Generator voltage 18.0 kV

- 0.85 power factor (lagging)

- Capability to 1.00 power factor (leading)

- Class .F. armature and rotor insulation

- Class .B. temperature rise, armature and rotor winding

- Generator bearings

- End shield bearing support

- Elliptical journal bearings

- Roll out bearing capability without removing rotor

- Insulated collector end bearing

- Online bearing insulation check

- Offline bearing insulation check with isolated rotor

- Monitoring Devices

- Two (2) velocity vibration probes at turbine end, one )1) at   collector end

- Provisions for key phasor-generator

- Provisions for permanent flux probe

- Proximity vibration probes

- Two probes per bearing at 45° angle

- Generator Field

- Direct cooled field

- Two-pole field

- Finger type amortissuers

5.2.2 Generator Gas Coolers

- Coolers shipped installed

- Generator gas cooler configuration

- Five (5) horizontally mounted simplex coolers

- Coolers located in generator base

- Cooler piping connections on left side as viewed from collector end

- ASME code stamp

- Single wall cooler tubes

- Victaulic cooler couplings

- Plate fins

- Cooling water manifold and isolation valves

- Generator gas cooling system characteristics

- Coolant temperature:		Not defined

- Generator capacity with one section out of service 80% with Class “F” rise

- TEMA class C coolers

- Maximum cooler pressure capability - 125 psi

- Fouling factor 0.0005

- Generator gas cooler construction materials

- 90-10 copper-nickel tubes

- Carbon steel tube sheets

- Carbon steel waterbox and coupling flanges with epoxy coating

- Aluminum cooler tube fins

5.2.3 Generator Lube Oil Systems and Equipment

- Bearing lube oil system

- Generator lube oil system integral with turbine

- Sight flow indicator

- Bearing lift oil system

- Stainless steel lift oil piping and tubing

- Lift oil supplied from turbine oil system

- Lube oil system piping materials

- Stainless steel lube oil feed pipe

- Carbon steel lube oil drain pipe

- Welded oil piping

5.2.4 Generator Grounding Equipment

- Neutral grounding equipment

- Neutral ground transformer and secondary resistor

- Mounted in terminal enclosure

- Motor operated neutral disconnect switch

5.2.5 Generator Temperature Devices

- Stator winding temperature devices

- 100 ohm platinum RTDs (resistance temperature detector)

- Single element RTDs

- Grounded RTDs

- Nine (9) stator slot RTDs

- Gas path temperature devices

- 100 ohm platinum gas path RTDs

- Single element temperature sensors

- Four (4) cold gas

- Two (2) hot gas

- GTG-2 (common cold gas)

- Bearing temperature devices

- Chromel alumel (type K) thermocouples

- Dual element temperature sensors

- Two (2) bearing metal temperature sensors per bearing

- Collector temperature devices

- 100 ohm platinum RTDs

- Single element temperature sensors

- Collector air inlet temperature sensor

- Collector air outlet temperature sensor

- Lube oil system temperature devices

- Chromel alumel (type K) thermocouples

- Dual element temperature sensors

- One (1) bearing drain temperature sensor per drain

5.2.6 Packaging, Enclosures, and Compartments

- Paint and preservation

- Standard alkyd beige primer

- High voltage bushings

- High voltage bushings shipped installed

- Six (6) ambient air cooled, high voltage bushings

- Generator terminal enclosure (GTE)

- Line-side terminal enclosure

- Terminal enclosure shipped separate

- Isolated phase bus duct connection

- Phase sequence R-C-L when looking at enclosure terminals

- Outgoing power connection on right side when viewed from collector end

- Lightning arresters

- Neutral terminal enclosure

- Neutral terminals integral with line-side terminal enclosure

- Neutral tie

- Collector compartment/enclosure

- Collector compartment/enclosure shipped separate

- Outdoor

- Collector/brush holding rigging

- Compartment lighting and outlets

- AC lighting

- Collector compartment

- Foundation hardware

- Generator shims

- Generator alignment key(s) - collector end

- Generator alignment key(s) - turbine end

- Generator alignment key(s) - axial

5.2.7 Hydrogen Systems and Accessories

- Hydrogen gas manifolds

- Auto purge gas purge control manifold

- Hydrogen/CO2 control valve assembly

- H2 Bottle manifold not provided

- CO2 bottle manifold not provided

- Seal oil system

- Control unit mounted in collector compartment

- Stainless steel seal oil feed pipe

- Carbon steel seal oil drain pipe

5.2.8 Electrical Equipment

- Motors

- TEFC motors

- Coated with antifungal material for protection in tropical areas

- High ambient motor insulation

- Motor heaters connected to ac power

- Extra severe duty motors

- Cast iron motor housings

- Heaters

- Generator stator heaters

- Generator collector heaters

5.2.9 Generator Excitation Systems, Static Components

- Bus fed static excitation with hot backup bridge

5.2.9.1 Excitation Module Features

- Control/monitor/display through TCP

- Voltage matching in turbine control system

- Power factor controller in turbine control system

- Var controller in turbine control system

- Selection of automatic or manual regulator

- Raise-lower of the active regulator setpoint

- Enter setpoint command

- Display field amps

- Display field volts

- Display transfer volts

- Built-in diagnostic display panel

- Automatic voltage regulator (AVR)

- Manual voltage regulator (FVR)

- Automatic and manual bi-directional tracking

- Reactive current compensation (RCC)

- Volts per hertz limiter (V/Hz LIM)

- Volts per hertz protection (24EX) (Backup to 24G)

- Over excitation limiter (OEL)

- Offline/online over excitation protection (76EX)

- Loss of excitation protection (40EX)

- Bridge ac phase unbalance protection (47EX)

- Under excitation limiter (UEL)

- Generator overvoltage protection (59EX)

- Generator field ground detector trip (64FT)

- VT failure detector (VTFD) (60EX)

- Field over-temperature alarm

- Field ground detector alarm (64FA)

- Exciter phrase voltage imbalance (47EX)

- Bridge over-temperature (26EX)

- Dual source internal bulk power supply

- Millivolt shunt for field

- Surge protection

- VT disconnect and CT shorting switches

- Two phase current sensing

- Three phase voltage sensing

- Single pole dc field contactor/bridge

- Thyristor bridge circuit filtering

- Shaft voltage suppressor circuit (mounted in panel)

- Field de-excitation circuit (with field discharge inductor)

- Bridge disconnect; AC no load

5.2.9.2 Performance

- 2.0 response ratio and 160% VFFL (100°C) ceiling @ Vt = 1.0pu

5.2.9.3 Excitation Enclosure Location

- Installed in LCI/EX compartment

5.2.9.4 LCI Features

- LCI located in LCI/EX compartment

- LCI disconnect switch (89SS)

- Located in generator terminal enclosure

- LCI fuse

- Located in compartment with LCI

5.2.9.5 PPT Features

- Freestanding oil-filled PPT for outdoor installation

- PPT fed from auxiliary bus

5.2.10 Generator Current Transformers and Potential

- Transformers

- Current transformers (CTs)

- C400 current transformers (CTs)

- Line side CTs

- CT 19A, C (excitation)

- CT 21, 22, 23 (generator differential relay)

- Neutral CTs

- CT1, CT2, CT3

- CT4, CT5, CT6

- CT7, CT8, CT9

- Potential transformers (PTs):		Fixed

- VT2, generator line side

5.3 Gas Turbine-Generator Controls and Electric Auxiliaries

5.3.1 Control Cab/Packaged Electric and Electronic Control Compartment (PEECC)

- Weatherproof, climate controlled, base mounted enclosure

- Supplemental wall-mounted air conditioner

5.3.2 Gas Turbine Control System Panel Features

- Triple modular redundant (TMR)

- Skid mounted control panel

- Auto/manual synchronizing module with synchronizing check function

- Generator stator overtemperature alarm (49)

- Droop control

- Load limiter

- Purge cycle

- Customer alarm/trip contact for CRT display

- Vibration alarm readout and trip

- Electrical overspeed protection

- Constant settable droop

- Power factor calculation and display

- Power factor control

- VAR control

- Manual set point preselected load

- IRIG-B interface (time signal by others)

5.3.3 Local Operator Station

- Commercial grade personal computer

- Color monitor

- Table top

- 17 in. screen

- Mouse cursor control

- Table top AT 101 keyboard

- Printer

- 24 pin dot matrix

- Display in English language

- RS232C two way serial link (MODBUS) via local HMI

5.3.4 Remote Control and Monitoring Systems

- RS232C two way serial link (MODBUS) via remote HMI

- Multi-unit remote HMI

- One per site

- Commercial grade personal computer

- Color monitor

- Table top

- 20 in. screen

- Mouse cursor control

- Table top AT 101 keyboard

- Printer

- Printer, color ink jet

- Power 120Vac 60 Hz

5.3.5 Rotor, Bearing and Performance Monitoring Systems

- Performance monitoring systems

- Performance monitoring sensors wired to gas turbine control system

- Performance calculations in <I>/HMI

- Vibration sensors

- Velocity vibration sensors

- Proximity vibration sensors

- Bently Nevada 3500 monitor

- With local display panel

- Relay outputs wired to gas turbine control panel

- Mounted with generator control panel

- Bearing thermocouples

- Bearing drain thermocouples

- Bearing metal thermocouples

- Borescope access holes

- 5.3.6 Generator Control Panel

- 5.3.6.1 Generator Control Panel Hardware

- Mounted in PEECC

- Skid mounted with turbine panel

- DGP with test plug capability

- DGP without ModBus communication interface

- DGP with communication interface

- DGP with IRIG-B interface

- DGP with oscillography capture

- DGP with redundant internal power supply

- Generator breaker trip switch (52G/CS)

- Humidity sensor readout

- Hazardous atmosphere detector readout

- Bentley Nevada vibration monitor(s)

5.3.6.2 Digital Generator Protection System (DGP)

- Generator overexcitation (24)

- Generator undervoltage (27G)

- Reverse power/anti-motoring (32-1)

- Reverse power/anti-motoring (32-2)

- Loss of excitation (40-1,2)

- Current unbalance/negative phase sequence (46)

- System phase fault (51V)

- Generator overvoltage (59)

- Stator ground detection (64G1)/(59GN)

- Generator over/under frequency (81O-1, 81U-1)

- Generator differential (87G)

- Voltage transformer fuse failure (VTFF)

5.3.6.3 Generator Protection Discrete Relays

- Synchronizing undervoltage relay (27BS-1,2)

- Reverse/inadvertent energization protection relay (50RE/86RE)

- Generator differential lockout relay (86G-1)

- Second generator lockout relay (86G-2)

5.3.6.4 Features Integrated Into Gas Turbine Control System

- Gas turbine control system with speed matching, synchronization and check

- Manual synchronization displayed on gas turbine control system <I> / HMI

- Auto/manual synchronizing module displayed on gas turbine control system <I> / HMI

- Load control in gas turbine control system

- Temperature indication for generator RTDs

- Generator voltage matching (90VM)

5.3.6.5 Generator Control Panel Metering

- Generator digital multimeter

- VM - Generator volts

- AM - Generator Amps: Phase 1,2,3 and Neutral

- MW - Generator MegaWatts

- MVAR - Generator MegaVARs

- FM - Generator frequency

- MVA - Generator MVA

- PF - Generator power factor

5.3.6.6 Generator Control Panel Transducers

- Generator watt/VAR transducer 4-20 mA output for input to TCP (96GG-1)

- Generator TCP/droop control transducer 4-20 mA output  (96GW-1)

- Generator watt/VAR transducer 4-20mA output for customer (96GG-2)

5.3.7 Generator Protection

- Generator electrical protection equipment

- Ground brush rigging

5.3.8 Batteries and Accessories

- Lead acid battery

- Single phase battery charger

- Second battery charger

- Battery and charger mounted in the PEECC

5.3.9 Motor Control Center

- MCC mounted in control cab/PEECC

- Tin-plated copper bus-work

- 65 kA bracing

- 480V 60 Hz auxiliary power

5.3.10 Motor Features

- TEFC motors less than or equal to 200 hp

- Coated with antifungal material for protection in tropical areas

- High ambient motor insulation

- Energy saver motors

- Extra severe duty motors

- Cast iron motor housings

- All redundant motors to be lead/lag

- Motor heaters

- Rated 110/120 volts, 50/60 Hz

- WP motors >200 hp

5.4 Services

- Technical advisory services: $1,750,000US credit available towards GE services.

- Documentation

- 1 set of English language service manuals per Unit, including

- Operation, Maintenance and Parts volumes

- Turbine maintenance tools (1 set per site)

- Guide pins (for removal or replacement of bearing caps, compressor casing and exhaust frame)

- Fuel nozzle wrenches

- Fuel nozzle test fixture

- Spark plug electrode tool

- Clearance tools

- Fuel nozzle staking tool

- Combustion liner tool

- Bearing and coupling disassembly fixture

- Generator maintenance tools (1 set per site)

- Rotor lifting slings

- Rotor removal equipment including shoes, pans, pulling devices

- Rotor jacking bolts

- Installation equipment

- Trunions for generator

- On permanent basis

- Jacking bolts for generator

- Foundation/installation washer and shim packs

| Approximate Shipping Dimensions & Weights- 1 PG7241FA Gas Turbine Generator Unit |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- |
| Gas Turbine |  |  |  |  |  |
| Item | Length Inches | Width Inches | Height Inches | Weight Pounds | Volume Cubic Feet |
| Box 1 | 351 | 158 | 161 | 377000 | 5167 |
| Load Coupling |  |  |  |  |  |
| Box 1 | 124 | 52 | 51 | 1000 | 190 |
| Coupling Guard |  |  |  |  |  |
| Box 1 | 80 | 36 | 46 | 3500 | 77 |
| Accessory Module |  |  |  |  |  |
| Box 1 | 360 | 126 | 158 | 7500 | 4148 |
| Summary Sheet Count |  |  |  |  |  |
| Box 1 | 240 | 96 | 102 | 13880 | 1360 |
| Box 2 | 60 | 44 | 48 | 4555 | 73 |
| Generator |  |  |  |  |  |
| Box 1 | 384 | 208 | 168 | 555300 | 7765 |
| Generator Loose Parts |  |  |  |  |  |
| Box 1 | 185 | 95 | 42 | 3625 | 427 |
| Box 2 | 73 | 66 | 58 | 840 | 162 |
| Box 3 | 46 | 27 | 76 | 845 | 55 |
| Box 4 | 41 | 15 | 9 | 302 | 3 |
| Box 5 | 60 | 57 | 10 | 1564 | 20 |
| Box 6 | 85 | 19 | 25 | 4485 | 23 |
| Box 7 | 134 | 78 | 89 | 3200 | 538 |
| Box 8 | 32 | 10 | 8 | 68 | 1 |
| Box 9 | 38 | 28 | 26 | 105 | 16 |
| Box 10 | 290 | 53 | 43 | 6000 | 382 |
| Box 11 | 108 | 72 | 92 | 12400 | 414 |
| Box 12 | 96 | 83 | 41 | 13000 | 189 |
| Box 13 | 94 | 83 | 65 | 7050 | 293 |
| Box 14 | 70 | 65 | 54 | 3800 | 132 |
| Box 15 | 196 | 24 | 7 | 550 | 19 |